利用报告系统错误诊断故障Wincc部分-赵根海

系统：win7 32位旗舰版；

编程软件：SETP7  V5.5  SP3；

上位软件：WINCC V7.0 SP3；

系统概况：CPU 416-2 DP及两个ET200M从站（DP地址分别为3、4）
[image: image1.png]@) Station Edit Insert PLC View Options Window Help

D@8 (& | Bedba 0 %R K

i o) uRL
1 PS 405 4A =
2 HCPU_416-2 DP
12 027 E
X1 0 wPr/oP
B HEcP 443-1
1 0 Ar1o
x1 P2 Rl Port 1
x1 P2 B[ Port 2
:
5 -

PROFIBUS(1): DP master system (1)

@@ m

[





PLC自动生成诊断块请见我之前的文章“利用报告系统错误诊断故障”， 

1、新建OS站（WINCC需要安装AS-OS选件），将OS集成在STEP7中；
1）将OS站编译；连接选择TCP/IP;

[image: image2.png]&) SIMATIC Manager - [reportsyserrwincc2 -- C:\Program Files\Siemens\Step7\s7proj\report_1]
Bp File Edit Insert PLC View Options Window Help
[0 || 4 L@ ke %" @ [ <No Filter > ~| 7 |R@|BE MW

& & reportsyserrvincc2 Object nane | Symbolic name | Type | size[author [Last modified | Comment
e-H SINATIC 400(1)
& @ cPy w62 P
57 Progran (1)
Sources
Blocks
A CP 443-1
2305(1)
Waard Compite 05 (5 || Selecthemorkcomecton
87 progran: 57 Progran(1)
Which S7 programs do you want to compile with which network connections?
s 5. | Subnet type | ¥inCC unit| Address|Station no. | Segnent no. |Rack no.
Operator stations and 57 programs:  Network comnection for 03(1): Tnd, Eth, il | [ o]
E 0s(1) 87 ... | Connections| Subnet [subr FROFIBUS(1) PROFIBUS PROFIBUS 2 0 0
ST Progran (1) 57 Progran (1) 2 Ethernet(1) Ind.
< ] ’
Comnection. ..
< Back Next > Finish | Cancel Help
Cancel
Press F1 to get Help. [PLCSIM(TCP/IP) [ [

=



  
2）打开OS，将计算机属性的启动项报警记录运行系统和图形运行系统打钩；
3)打开报警记录，选择用户文本块添加块3，此步骤非常关键；
[image: image3.png]2} RBIER - [0S()]
) SIEE) ME((V) EEM) TET) #FEiH)

E=RIEE

LBNELY

HEXAE HEER

1610612739
1610612740 $&i% b
1610612741 $&i% b
1610612742 $&i% b
1610612743 $&i% b
1610612744 $&i% b
1610612745 $&i% b
1610612746 $&i% b
1610612747 $&i% b
1610612748 $&i% b
1610612749 $&i% b
1610612750 $&i% b
1610612751 $&i% b
1610612752 $&i% b
1610612753 $&i% b
1610612754 $&i% b
1610612755 425 EEr

PR R R R R R R R R R R R R R e

[ju=zs  |He@
S7$Program(:0
S7$Program(:0
S7$Program(:0
S7$Program(:0
S7$Program(:0
S7$Program(:0
S7$Program(:0
S7$Program(:0
S7$Program(:0
S7$Program(:0
S7$Program(:0
S7$Program(:0
S7$Program(:0
S7$Program(:0
S7$Program(:0
S7$Program(:0
S7¢Proaram( 0

[z

[prste

o

cooocoooooooooooo

sz

S7 Program(1
7 Program(1
7 Program(1
7 Program(1
7 Program(1
7 Program(1
7 Program(1
7 Program(1
7 Program(1
7 Program(1
7 Program(1
7 Program(1
7 Program(1
7 Program(1
7 Program(1
7 Program(1
<7 Proaram(1

: 3
Rack 0, Slot 1: @1Wt#ErrTextLib@\nN:

Rack 0, Slot 2.2: @1W%t#ErrTextLib@\nN&

Rack 0, Slot 3: @1Wt#ErTextLib@\nN:

Rack 0, Slot 3.1: @1W%t#ErrTextLib@\nN&
Rack 0, Slot 3.2: @1W%t#ErrTextLib@\nN&

Rack 0, Slot 3.2: @1W9%t#ErrTextLibExP!
Rack 0, Slot 3.2: @1W9%t#ErrTextLibExP!
Rack 0, Slot 3.2: @1W9%t#ErrTextLibExP!

Rack 0, Slot 3.3: @1W%t#ErrTextLib@\nN&
Rack 0, Slot 3.3: @1W%t#ErrTextLibExP!

Rack 0, Slot 3.3: @1W%t#ErrTextLibExP!

Rack 0, Slot 3.3: @1W%t#ErrTextLibExPNES
PB slave 3 on PB system 1, Slot 4: @1W%}5
PB slave 3 on PB system 1, Slot 4: @1W%}5
PB slave 3 on PB system 1, Slot 5: @1W%{5





设置消息类别下错误-报警；故障出现红色；故障出现绿色；故障已确认黄色；
[image: image4.png]o3 REER - [0S()]
SeHF) BEE WEY) M) TEM #EH)
|| % LENEL
= e (&) (&)
= s
SN
RE
JAHE
BEHE
HEEHEARNER, TAENERNE (r
[ wme | ms || Z9@ |





新建画面，添加报警控件；双击控件打开消息列表将块3添加进来；很关键；
[image: image5.png]P EV4RIEER - [NewPdI0.PdI]
Jr ) REE WEV) H5IA) TR EOW) BEH)

Omom»[X

am

L m
E)
=
0

100000 %

I

HAAR (22 (Ao F(8 2w

T @Artal Unicode S

[ wincc AlarmControl

WinCC AlarmControl Bt

10\08\17

HE

L« ] [me)lar]

BrEifE

wE ]

[ == ]





将系统参数中的单元该为PLCSIM(TCP/IP)，需要重启WINCC；也是很关键的一步；
[image: image6.png]& WinCCExplorer - C:\Program Files\Siemens\Step7\s7proj\report_1\wincproj\OS(1\OS(1).mep [ &3]

) SWEE) WE((V) TEM FEH)

Oomy[x
=% 0S(1) 28 brER
HEH xt %
e BAMRE
REEE
£} SIMATIC S7 PROTOCOL ¢ FHBH - TCP/IP
Industrial Ethernet souaric s7[BE
Industrial Eth
industrial Ethernet () e

MPIL

Named Connections

PROFIBUS

PROFIBUS ()

1 Slot PLC

Soft PLC

i} TCP/IP
)

A EmEE

o TR

of BREER

=HBIER

RERES

PSS 2

B xam

I

CP ZA/ B

BEREERO):

v BEaE @)

{EdbabiE
[~ S

free/re

I (TCF/IP) =~

WA EIREEFIN IR PEEREREE .

8





5、打开PLCSIM触发3#从站4#槽AI模块移除、插入故障；
[image: image7.png]@8 HW Config - [SIMATIC 400(1) (Configuration) -- reportsyserrwincc2]
B station Edit Insert PLC View Options Window Help
D88 &S| 6 e | dd B8

i (0) vR1 @ 'S7-PLCSIM1  SIMATIC 400(1)\CPU 416-2 DP EEr=]
e e File Edit View Insert PLC Execute Tools Window Help
5 e L FROFIBUS(1): DP master system (1) D& EE [pesmcr/n~| » R BBEw R EEEEEa
X1 HPI/DP
B HEcP 443-1
1 0 Ar1o @ 3) I
x1 1 k|l Port 1 m m
11 P2 R[d Port 2
+
g = E RuN
BN, ™ SToP  wRes
Insert/Remove Module Interrupt OB (83)
Module Status
© Module removed or not responding
@ Module insertect madule type OK
© Module insertedt inconrect module type <
<[ i  Module insertedt type ID cannotbe readt v
 Module insertedt enor in modle parameter assignment
® 9 @ miss
8. Module ... |Order Number ... | T Add... |0 Address |Comment Module address : [piw512]
T
7@ 157 57 15514000050 |16575% oK spply | cancel | Hep |
3
4 [ az2x1z GEST 7KBOO-0ABO
5 | AvzxizBit BEST_552-5HBOO-0ABO 512...515
3
7
5
5
10
1]

Press F1 to get Hell

23:35

2017\8\10 28|




画面显如下和仿真一致；
[image: image8.png]PEEENsEsaERE ¢ @EHE

EE?]

11\08\17
11\08\17
11\08\17
11\08\17
11\08\17
11\08\17

PROFIBUS (1) : DP master system (1)
PROFIBUS (1) : DP master system (1)
PROFIBUS (1) : DP master system (1)
Slot 4: Wrong module inserted Name:
Slot 4: Wrong module inserted Name:
Slot 4: Wrong module inserted Name:

06:43:45 _16PB
07:24:50 _16PB
07:25:19 _16PB
07:26:10 _16PB
07:26:25 _16PB

system 1: Failure Name:
system 1: Failure Name:
system 1: Failure Name:
slave 3 on PB system 1,
slave 3 on PB system 1,
slave 3 on PB system 1,

IM 153 Module: AlI2x12Bit |/0 address:
IM 153 Module: AlI2x12Bit |/0 address:
IM 153 Module: Al2x12Bit |/0 address: S7

RE: 0 EHEIA: 0 DI 0 UE: 0




不足：报警时间不同步（改为协调世界时即可）；自动生成的块多复杂；只能生成一次；程序块删除再生成容易出问题；
[image: image9.png]A WinCCEaRS -

[ wincc AlarmControl

0RIFREE

e BEalfel s Y BAe B

EE7] i

SENEEREN

10

12
13
14
15
16
17
18
19
20
21

22
23
24
25
26

5 B 3 HELA [HiEE

HARE
[OF=" 14
© iR (UTC)

[a2
ik

TERE: 1 fEREIA: 1 OB O SF: 1

EEERY





优点：不用编程、自动生成；
