
SM331 INFORMATION COLLECTION
SLC A&D CS
April 2004
41.
如何获得西门子自动化与驱动产品的资料及在线技术支持


42.
西门子技术支持热线


53.
需要SM331的产品手册


54.
标准及认证


55.
SM331搬运、存储、运行的环境要求


66.
SM331常用信息


67.
缩写词含义


68.
如何使用SM331


79.
在STEP 7的硬件目录里找不到想要配置的硬件


810.
SM331上不使用的通道的接线


811.
如何在STEP 7中设置SM331的参数并访问其通道


811.1.
如何在HW Config中设置SM331的参数


911.2.
在程序中对模拟量输入的访问


1012.
如何连接传感器及外部电源到SM331模板


1013.
连接二线制变送器到SM331模板


1013.1.
两线制信号(2DMU)与四线制信号(4DMU)的区别


1013.2.
如何连接两线制变送器到只能接入四线制信号的模板


1013.3.
两线制信号与四线制信号接线的注意事项


1013.4.
不同类型传感器到SM331-7Kx0x的接线实例


1114.
连接热电偶到SM331模板


1114.1.
为什么要用补偿盒对SM331进行外部冷端补偿及怎样补偿(6ES7 331-7KFxx-0AB0及6ES7 331-7KBxx-0AB0)


1114.2.
热电偶量程转换


1115.
连接热电阻到SM331模板


1115.1.
热电阻测量原理及连接两线、三线、四线热电阻到6ES7 331-7Kxxx-0AB0


1115.2.
量程转换


1215.3.
为什么用数字万用表测量不到SM331模板测量电阻值的电流


12请点击http://www4.ad.siemens.de/WW/view/en/13963555 阅读在线FAQ。


1215.4.
连接三线制热电阻到6ES7331-7PF00-0AB0的注意事项


1216.
连接HART协议仪表到SM331模板


1216.1.
如何连接支持HART协议的仪表到SM331模板


1316.2.
怎样用SM331(6ES7331-7TB00-0AB0)读HART仪表的数据


1316.3.
连接HART 仪表到常规S7-300 模拟量输入模板


1316.4.
6ES7331-7TB00-0AB0不用通道的设置


1317.
怎样设置并修改SM331的分辨率


1318.
STEP 7 中用于读取模拟量的功能块


1319.
读出的模拟量值超限


1320.
SM331 SF灯亮


1421.
直接将来自0区或1区的传感器信号接入S7-300 Ex(i) 模板


1422.
与SM331有关的OB块




1. 如何获得西门子自动化与驱动产品的资料及在线技术支持
首先,建议您访问Siemens A&D的产品与技术支持网站 http://www4.ad.siemens.de/ 

[image: image1.png]Fle Edt View Favortes Tools Help

Gack - > - @ [ A | Qoearch (GiFavortes iveda B | BN 5 5 (R

asass [ g o s s ]

SIEMENS . us [Engisn [

e

pport Information

Automation and Drives

For MySupport | would iketo: Bl Loain (B Reaister
Service & Support

WARBRETHE
News and Oniine:Help
Cortacts workawie Product Support
Here youswil find al our Products and Systems
Field Service N/ ==
Spare Parts
Services

Technical Support

Errene) You need a senice specialist, a spare part, an expert o

consult or you simply have a question.

TECHUCAL ~ TECHMCAL  SPAREPARTS/ FELD
Newsletter SUPPORT  CONSLLTING REPARS  SERVICE
Forum

Support Shop
Expert Furchase the following products online with the AV Card
Communication

STANDARD  SUPPORT

e O TOPDOWNLOADS  AV-CARD





或者，致电010-64721888转3785 索取资料。

如需设备选型及订货，请联系当地西门子分销商。分销商联系方式可致电010-64719990获得。

2. 西门子技术支持热线

如有无法自行解决的技术问题，请拨打西门子技术支持热线010-64719990登记，等待西门子技术支持工程师回复。我们会在8小时内予以响应。

请注意在登记问题时尽量准确地描述所使用产品的类型，以便尽快得到负责该产品的工程师的帮助。
3. 需要SM331的产品手册
请点击 http://www4.ad.siemens.de/WW/view/en/8859629 下载。
4. 标准及认证

1. CE approval
2. UL approval
3. CSA approval
4. FM approval
5. [image: image2.png]



6. Identification for Australia
7. IEC 61131
8. Shipbuilding approval
详细信息请参见模板手册。

5. SM331搬运、存储、运行的环境要求

标准模板运行状况下要求的气候条件参见下表：

[image: image3.png]Climatic Conditions.

Permitted range

Remarks

Temperature:
horizontal installation:
vertial instalation

oM 010 60°C
from 010 40°C

Relative humidity

101095 %

Non-condensing, corres-
ponds to relative humi-
ity (RH) Class 2 accor-
dingto IEC 61131, Part 2.

“Atmospheric pressure

108010 795 hPa

Cormesponding to an alti-
tude of~1000 to 2000 m

Concentration of contami-
nants

S0z <0.5 ppm;
RH <60 %, non-condensing
HaS: < 0.1 ppm:

RH < 60 %, non-condensing

Test: 10 ppm; 4 days

Test: 1 ppm; 4 days





SIPLUS S7-300模板应用于扩展的环境条件下，扩展的环境条件描述如下：

· Operation possible at temperatures from –25C to +60C

· Occasional, brief condensation permitted

· Increased mechanical stress permissible
详细信息请参见模板手册。
6. SM331常用信息

SM331模板是西门子S7-300系列PLC中的模拟量输入模块，常用模板的信息请参见

[image: image4.wmf]"SM331 

Characteristics"


7. 缩写词含义
FAQ: Frequently Asked Questions 经常问到的问题

M +: Measuring lead (positive) 信号线（正）

M–: Measuring lead (negative) 信号线（负）

MANA: Reference potential of the analog measuring circuit 模拟量输入回路的参考电势

M: Ground terminal 接地端

L +: Terminal for 24 VDC supply voltage 24VDC电源接线端

UCM: Potential difference between inputs and reference potential of the MANA measuring circuit 

信号输入端与MANA间的电势差

UISO: Potential difference between MANA and M terminal of CPU MANA与CPU的M端间的电势差

I +: Measuring lead for current input 电流输入测量端

U +: Measuring lead for voltage input 电压输入测量端

如何使用SM331

请点击http://www4.ad.siemens.de/WW/view/en/17473828 下载 Getting Started of SM331 4~20mA手册。

使用SM331的基本步骤如下：

1. Select the module 模板选型
2. With some analog input modules: set the measuring method and measuring range by means of the measuring range module 通过量程卡确定测量类型、测量范围
3. Install the module in the SIMATIC S7 network 安装模板
4. Assign parameters to module 设置参数

5. Connect measuring sensor or loads to module 连接传感器到模板
6. Commission configuration 调试
7. If commissioning was not successful, diagnose configuration 如调试出错，做相应的诊断
8. 在STEP 7的硬件目录里找不到想要配置的硬件

如果在STEP 7 的硬件目录中找不到想要配置的硬件，解决办法如下：

1. Installing Hardware Updates
As of STEP 7 V5.2, you can subsequently install components for the Hardware Catalog. In this way you can use individual components such as new CPUs or new I/O devices in the current version of STEP 7 without having to install a new service pack.
Procedure:

· Select the menu command Options > Install HW Updates. 

· In the dialog that appears, specify whether the HW update should be downloaded from the Internet or copied from a CD or 
whether you want to install updates that have already been download (selection available) 

2. Select the component to be installed and then click the "Install" button. 
3. 如果您使用的是STEP 7 V5.1或者更低的版本，而在STEP 7的硬件目录里找不到想要配置的硬件，那么首先建议您到http://www4.ad.siemens.de 网站上下载STEP 7的补丁程序，如SP6 for STEP 7 V5.1或SP1 for STEP 7 V5.2并安装，如果仍然找不到想要配置的硬件，就必须找当地的分销商升级STEP 7软件到最新的版本。目前STEP 7的最新版本为V5.3。

9. SM331上不使用的通道的接线
请点击http://www4.ad.siemens.de/dnl/DkxODg4MQAA_42382/besch_e.pdf 了解详细信息。

或参考下文：
[image: image5.wmf]"unused channel 

wiring"

。
10. 如何在STEP 7中设置SM331的参数并访问其通道

10.1. 如何在HW Config中设置SM331的参数

通常，在硬件配置中SM331的属性设置包括General, Addresses, Inputs三项，见下图：

[image: image6.jpg]Soner] At o |

= - e
e o 5 s o7
Diogrosics
S Disgroste: {1 S |
wihCheckfowieBese [ T || T || T || T |
T

Measuing Type:

FE_—F " F F
Measuing Rarge: oy |—./mv !—‘/mv oy

Posiion af Measuing
Flange Selecton Mode: 18] (8]

rtererence iequency  [50Hz [50Hz [50Hz Sz

Tiigger for Hatdware Ineupt Channel0  Channel2
High Limit

I 1





在General中包含对模板信息的描述。在Addresses中定义该模板各通道在系统中的I/O地址，在程序中可以用PIW的方式访问，如PIW218。在Inputs中包含诊断中断、硬件中断、断线检测、测量类型、测量范围、量程卡等的相关设置与信息，详细描述请点击右下角Help键。
其中一个参数需要注意：

Integration Time/ interference frequency suppression
The frequency of the AC power supply network can interfere with the measurement values. With this parameter you specify the frequency of your power supply on site.

• Interference frequency: Select your power frequency (50 Hz or 60 Hz)

The integration time implicitly determines:

·
The interference frequency suppression

·
The resolution

The following table illustrates this relationship:
[image: image7.png]Resolution [Interference [ lntegration time [ Basic execution time
frequency

EES 0z T5ms s

260 EES 55 ms L

260 EES ELS TT6ms

TABR EE3 T00TS EECS





10.2. 在程序中对模拟量输入的访问

在程序中对模拟量输入的访问分为直接地址及过程映像两种。直接地址即直接访问在HW Config中定义的地址，如该通道地址为120，则在程序中访问PIW120(PI: Peripheral Input)即可。过程映像则是在程序中直接访问CPU的process image，如该通道地址为120，则在程序中访问IW336即可。两者差别如下：

Compared with direct access to the input/output modules, the main advantage of accessing the process image is that the CPU has a consistent image of the process signals for the duration of one program cycle. If a signal state on an input module changes while the program is being executed, the signal state in the process image is retained until the process image is updated again in the next cycle. The process of repeatedly scanning an input signal within a user program ensures that consistent input information is always available. 
Access to the process image also requires far less time than direct access to the signal modules since the process image is located in the internal memory of the CPU.
11. 如何连接传感器及外部电源到SM331模板

请参见模板手册中相应订货号的模板的外部接线图。

12. 连接二线制变送器到SM331模板
12.1. 两线制信号(2DMU)与四线制信号(4DMU)的区别

参见  
[image: image8.wmf]2线制传感器和4线

制传感器说明FAQ�


或点击http://www4.ad.siemens.de/WW/view/en/188821 阅读在线FAQ。

12.2. 如何连接两线制变送器到只能接入四线制信号的模板

请点击http://www4.ad.siemens.de/WW/view/en/18475312 阅读在线FAQ。

12.3. 两线制信号与四线制信号接线的注意事项
2-wire measuring transducer: 

· Connect Mana to M (jumper between Pins 11 and 20) and jumper Pins 10 and 11. 

· Short-circuit the unused channels of a channel group or jumper them with a 3.3 kohm resistor. 

4-wire measuring transducer: 

· Connect all Mx- to Mana and Pin 10 to Pin 11. 

· Connect the unused channels of a channel group in series and connect Mx- to Mana. 
12.4. 不同类型传感器到SM331-7Kx0x的接线实例

请点击http://www4.ad.siemens.de/WW/view/en/264773 阅读在线FAQ。

13. 连接热电偶到SM331模板
13.1. 为什么要用补偿盒对SM331进行外部冷端补偿及怎样补偿(6ES7 331-7KFxx-0AB0及6ES7 331-7KBxx-0AB0)

请点击 http://www4.ad.siemens.de/WW/view/en/18272332 阅读在线FAQ。
13.2. 热电偶量程转换

各分度的热电偶量程转换表，请参见模板手册。

14. 连接热电阻到SM331模板

14.1. 热电阻测量原理及连接两线、三线、四线热电阻到6ES7 331-7Kxxx-0AB0

请点击http://www4.ad.siemens.de/WW/view/en/8460832 阅读在线FAQ。

14.2. 量程转换

各分度的热电阻量程转换表，请参见模板手册。

常用的PT100热电阻量程转换表如下：

[image: image9.png]Analog value representation for RTD Resistance Temperature Detectors Pt x00

standard

Table 4-16 Analog value representation for RTD Resistance Temperatur Detectors PT 100, 200, 500,

1000
PUx00 Units PUx00 Units PUx00 Units
standard standard standard
n'C  ecimal | hexa- | ' [decimal| hexa- | K [ Tgecimal| hexa- | Range
1 digit decimal | (1 digit decimal | (1 digit= decimal
=01 04K)
10000 | 32767 | TFFRy | > 1820|3277 | TFFRy |- 12732 |30767 | TFFRy | Overfow
0000|1000 | 2710y | 18320 | 1eaz0 |70y | 127a2 | 1z7ez | atEce
Ovarranga
01 [sso1 |21 [1se21  [1se21 [sposy 1233 [12ss [men
w00 [0 |2tk | 120 | o |sook a2 |naw |zeen |
2000|2000 |Fsan, |20 | |rag, |732 2 |ac, |
T R T T PR T v EEE) 731|208y
Undertang
2430 | o430 |Femy | 4054 |soss |Foomy |302 s |12Ew
<2430 | o27oe |00y | <4054 | s27ee |00 | <302 |a2re6 | 000y | Underiow





[image: image10.png]Analog value representation for RTD Resistance Temperature Detectors Pt x00
climate

Table 4-17 Analog valus representation for RTD Resistance Temperature Detectors Pt 100, 200, 500,
1000

Prx00 Units Prx00 Units
climate climate
decimal | hexa- | IM'F  [decimal | hexa- Range

decimal | (1 dii decimal
0.01°F)

a7 | 7FFEn | Sato0 | 527e7 | 7R | Overow

15500 |scBcy |atio0 | atoo | 797ck

Overranga
1001 [13001 |s2ce, |2e801  [2es01 |eem,
000 | 13000 | 3208 | 2600|2860 | e7Emy

Rated range
12000 | 12000 |D120,, | -t8400 | tea00 |es20,
12001 | 12001 | DiiFy | 18401 | 16401 | BB1Fy

Underrangs.

14500 | -14500 | C7scy |-22000 | -22000 | AGSCH

<1500 | 2768 |00y | <-22900 | 2768 | 5000 | Undariow,





本文仅列出常用的Pt电阻的量程转换表，如果使用Cu电阻或Ni电阻，请参见模板手册。
14.3. 为什么用数字万用表测量不到SM331模板测量电阻值的电流 

请点击http://www4.ad.siemens.de/WW/view/en/13963555 阅读在线FAQ。

14.4. 连接三线制热电阻到6ES7331-7PF00-0AB0的注意事项

在连接三线制热电阻到6ES7331-7PF00-0AB0这块模板时有一个注意事项，在模板手册中有一条说明：The resistance measurement for a three-conductor connection is performed every 5 minutes。也就是说，在三线制热电阻接入这块模板时，第一次从模板读到数据需要5分钟的时间，因为模板每5分钟计算一次热电阻的长线补偿值。

15. 连接HART协议仪表到SM331模板
15.1. 如何连接支持HART协议的仪表到SM331模板


[image: image11.wmf]"HART Config for 

S7-300/400"


15.2. 怎样用SM331(6ES7331-7TB00-0AB0)读HART仪表的数据

[image: image12.wmf]怎样读HART仪表的

数据


15.3. 连接HART 仪表到常规S7-300 模拟量输入模板
请点击http://www4.ad.siemens.de/WW/view/en/2043180 阅读在线FAQ。

15.4. 6ES7331-7TB00-0AB0不用通道的设置
请点击http://www4.ad.siemens.de/WW/view/en/14034159 阅读在线FAQ。

16. 怎样设置并修改SM331的分辨率
请点击 http://www4.ad.siemens.de/WW/view/en/42510阅读在线FAQ。
17. STEP 7 中用于读取模拟量的功能块

You can use the blocks FC 105 “SCALE” (Scale Values) for reading analog values in STEP 7. You will find the FC in the standard library of STEP 7 in the subdirectory called “TI-S7 Converting Blocks” (for a description, refer to the STEP 7 Online Help for the FC).
18. 读出的模拟量值超限
请点击 http://www4.ad.siemens.de/WW/view/en/11966082 阅读在线FAQ。

通常，从SM331的通道中读出7FFF超限值的现象可以通过正确的外部接线避免，各种信号及各订货号模板的接线参见本文相关章节。如果在外部接线完全满足模板要求的情况下，仍然出现读数超限，则有可能是信号源接地不好、信号电缆敷设过程中有电磁干扰等原因造成M-与Mana间电势差Ucm过大。这种情况下建议采用有源信号隔离器。

19. SM331 SF灯亮

SM331 SF灯亮表明硬件故障。可能的原因如下：模板所需24VDC电源未正确接入；前连接器未插到位；总线连接器未连好；有硬件中断产生（断线、超限），量程卡所插的方向与HW Config中的设置不符，等等。

在线察看模板信息的方法参见下图：

[image: image13.jpg]iration)
msmn Ed_Insert | pLc. Vew Options Widow Helo

3(2-{® (3 ¢ Dawn\aad el

Dorload e dert st
. Lpload e ertfcation o PG
OGN e eRe ) promiaus(i) OP master ssen

iy o —

Modue Information, CtrD

e

5ok Tie of Day,
Prepare Line Diagnostics:
Monitor Mody

Update Firmpare,
Assign Ethernet Address.

PROFIEUS »





20. 直接将来自0区或1区的传感器信号接入S7-300 Ex(i) 模板

请点击http://www4.ad.siemens.de/WW/view/en/12346645 阅读在线FAQ。
21. 与SM331有关的OB块
	Type of Interrupt 
	Organization Block 
	Priority Class (Default) 
	See also （STEP 7 Online Help)

	Main program scan 
	OB1 
	1 
	Organization Block for Cyclic Program Processing (OB1) 

	Cyclic interrupts 
	OB30 
OB31 
OB32 
OB33 
OB34 
OB35 
OB36 
OB37 
OB38 
	7 
8 
9 
10 
11 
12 
13 
14 
15 
	Cyclic Interrupt Organization Blocks (OB30 to OB38) 

	Hardware interrupts 
	OB40 
OB41 
OB42 
OB43 
OB44 
OB45 
OB46 
OB47 
	16 
17 
18 
19 
20 
21 
22 
23 
	Hardware Interrupt Organization Blocks (OB40 to OB47) 

	Redundancy errors 
	OB70 I/O Redundancy Error (only in H systems) 
OB72 CPU Redundancy Error (only in H systems) 
	25 
28 
	"Error Handling Organization Blocks (OB70 to OB87 / OB121 to OB122)" 

	Asynchronous errors 
	OB80 Time Error 
OB81 Power Supply Error 
OB82 Diagnostic Interrupt 
OB83 Insert/Remove Module Interrupt 
OB84 CPU Hardware Fault 
OB 85 Program Cycle Error 
OB86 Rack Failure 
OB87 Communication Error 
	25 
(or 28 if the asynchronous error OB exists in the startup program) 
	Error Handling Organization Blocks (OB70 to OB87 / OB121 to OB122) 

	Startup 
	OB100 Restart 
(Warm start) 
OB101 Hot Restart 
OB102 Cold Restart 
	27 
27 
27 
	Startup Organization Blocks (OB100/OB101/OB102) 

	Synchronous errors 
	OB121 Programming Error 
OB122 Access Error 
	Priority of the OB that caused the error 
	Error Handling Organization Blocks (OB70 to OB87 / OB121 to OB122) 


各OB块详细信息请参见STEP 7在线帮助。具体方法为：打开STEP 7 Help, 在Index中搜索关键字OBxx，即可查到该块的功能、可访问的临时变量等。







































































































































_1143546763.doc
模拟量模板未使用通道的端子接线

		测量范围

		模板型号



		

		6ES7 7KXXX-0AB0

		6ES7 334-0CE00-0AA0

		6ES7 335-7HG00-8AA0



		电压, 1... 5V

		未使用的输入通道应与另一个使用的通道并行连接模拟输入信号，这样并联会减小测量回路的输入阻抗。例如，将两个通道串联起来，输入电阻为原来的1/2。

		无该测量范围

		无该测量范围



		电压, 其他范围

		未使用的输入通道应被短路连接，同时将M- 端与Mana端连接。

		未使用的输入通道应被短接，同时将M- 端与Mana端连接。

		未使用的输入通道应被短路连接。



		电流, 4线制, 4 ... 20mA

		未使用的输入通道应与另一个使用的通道串行连接模拟输入信号，这样会增大测量回路的输入阻抗。例如，将两个通道串联起来，输入电阻为原来的2倍。

		无该测量范围

		未使用的输入通道应与另一个使用的通道串行连接模拟输入信号，这样会增大测量回路的输入阻抗。例如，将两个通道串联起来，输入电阻为原来的2倍。



		电流, 4线制, 其他范围

		未使用的输入通道应被短路连接，或者，您也可以将未使用的通道与已使用的通道串联，如果将两个通道串联起来，输入电阻为原来的2倍。

		未使用的输入通道应被短路连接，或者，您也可以将未使用的通道与已使用的通道串联，如果将两个通道串联起来，输入电阻为原来的2倍。

		未使用的输入通道应被短路连接，或者，您也可以将未使用的通道与已使用的通道串联，如果将两个通道串联起来，输入电阻为原来的2倍。



		电流, 2线制,4... 20mA

		2线制传感器是从模板的通道上获取工作电流，正因为此，应当在未使用通道上连接一个1.5—3.3千欧姆的电阻。

		无该测量范围

		无该测量范围



		电阻值测量

		将未使用的通道开路，不接线

		无该测量范围

		无该测量范围



		PT100

		将未使用的通道开路，不接线

		无该测量范围

		无该测量范围





注意: SM33x模板中每一组通道共用一个A/D采样电路，因而以上措施针对的是同一组中的各个通道，不同组之间的通道不应采用以上连接方法。如果模板上的某组通道不使用，则需在用STEP 7做HW Config时，取消该组通道的激活状态，即选择deactivated，而在模板接线时将该通道开路即可。


_1143556331.doc
FAQ ( 常问问题 )


Case No.:

产品类型：SM331


问题：两线制电流和四线制电流的区别?


用户在使用电流传感器或者电流变送器时，经常分不清什么是两线制电流，什么是四线制电流。绝大多数的用户认为，只要接两根线的电流信号就是两线制电流信号，这样的观点是不正确的。


两线制电流和四线制电流都只有两根信号线，它们之间的主要区别在于：两线制电流的两根信号线既要给传感器或者变送器供电，又要提供电流信号；而四线制电流的两根信号线只提供电流信号。因此，通常提供两线制电流信号的传感器或者变送器是无源的；而提供四线制电流信号的传感器或者变送器是有源的，因此，当您将您的模板输入通道设定为连接四线制传感器时，PLC只从模板通道的端子上采集模拟信号，而当您将模板输入通道设定为连接二线制传感器时，PLC的模拟输入模板的通道上还要向外输出一个直流24V的电源，以驱动两线制传感器工作。要想正确设置模拟量输入模块的量程，您必须首先确定传感器或者变送器的信号类型。



_1143353978.doc
FAQ ( 常问问题 ）


提供者：崔坚


提供时间：24/07/01


产品类型：SIMATIC\SIMATIC S7-300


问题：怎样用SM331(6ES7331-7TB00-0AB0)读HART仪表的数据？


解答：1）首先必须在ET200M中插入SM331，并用PDM软件组态SM331的参数。


2）如果需要读主要变量，可以直接用PIW读出。如果需要读出最高4个预先定义的动态变量（包括主要变量、第二变量等），通过一个HART通道，则需调用SFC58为命令“3”，写入到SM331的数据区中（命令请求），用SFC59读出SM331的响应值。


调动例子：


写命令：


       Call SFC58             


       REQ:=M2.1                     （1为请求）


       IOID:=B#16#54               （SM331是一个混合模块）


       LADDR:=W#16#0            （SM331的地址）


       RECORD:=B#16#A          （第一个客户端命令为10）


       RECORD:=P#DB1.DBX0.0 Byte 240


       RET_VA2:=MW4             （调用SFC58，错误返回值）


       BUSY:=M6.1                   （BUSY＝1，写没完成）


RECORD：总共234个字节，第二个字节为命令3，读4个预先定义的值。 


读响应值：


       Call SFC59


       REQ:=M2.2


       IBID:=B#16#54


       LADDR:=W#16#0


       RECNUM:=B#16#C           （响应为13）


       RET_VAL:=MW8


       Busy:=M6.2


       RECORD:=P#DB2.DBX0.0 Byte 240


RECORD：响应数据从第12个字节到第240个字节。                  


_1143354807.doc
Following is layout of hardware config for S7-300 with HART input/output module


Abstract: PROFIBUS-DP, IM153-2, 6ES7 331-7TB00-0AB0 (INPUT), 6ES7 332-5TB00-0AB0 (OUTPUT)


[image: image1.jpg][SIMATIC 300(2) (Configur: =18]x|
B Staton Edt Insert PLC vew Options Window e ETET]

DlfE 8] 8| o) dla F=] %) x|

jgmnb [ —

1M 1531, Release 7
1M 1532
1M 1532
1M 1532

3 Al300
« | 531 Ao

[ HART FidD)

4] (1) M1532, recndont SM 331 41221 2B
S 331 A28

S 331 A28
S 331 A28
SH 331 A2A1281
SH 31 A
SH 331 ABKIZ8
SH 331 ABKI28
SH 331 ABKI281
SH 331 ABK13B
SH 331 AGK13B
SH 331 A1 481
SH 331 AGKIEBR
SH 331 AeKIEBR
SH 231 ABATD

I AIZaART, Ex[5EG7 331-7TB00-0AB0[336...951 [336..351 S 331 AIBATC

M 331 AIBATC/ +
82 Kl | >

s [[{ AOZ:HART, Ex [6ES7 332 5TB000AB0 (352367 [362_367 oEe T 2
V1250, +/.5V, +/ 10V: Omite. ~—(—
4 A to 20 mh, +/- 20 m;

|ieconfguratie cnine
Press F to get Heh. e
Mstart||| & B ] || Dinbox...| Bysrcm..| Padob. | fassis...| €1ae0s..| Epepit...| Boma... [Fhrwe.. Fluntte..| B E 7 G ab=

T T ET |
&0 ET 200
% |’F e~ FROFIBUS(); DP master system (1) ﬁi‘ 153
1 g M 1531
2 DIB/DOGHDCINV/TEA g M 1531
5 [ AlsTciaRTD.Ex @M 183 &@03IM 183 3 M 1531
1 @ IM 1531, Aelease 15
1 @ IM 1531 Felease 16
& 1 @ IM 1531 Aiekase &

QAddress | Comment

[256...271 =

Ot Number
[6ES7 331-7TB00-0ABO

HART Field Device
4.2 [[§ HART Field Device
5 [[f ADZMHART. Ex __[GES7 3325TB000AB0 _[288...303 [288...303
51 [[§ HART Field Device
52 [[§ HART Field Device

AIZRHART. Ex

G657 331-7TB00-0AB0 [304._319 [304._319

[ AD2«HART. Ex _ [6ES7 332.5TB00-0AB0_[320...335 [320..335

i
i
i
i
i
i
i
i
i
i
i
i
i
i
i
i
i

32 | |







SM331支持HART协议仪表的模板的订货号为6ES7 331-7TB00-0AB0，该模板有两个输入通道。对该模板的配置要求如下：


该模板必须安装在ET200M的从站上，且接口模板必须为IM153-2。



_1143352012.doc
[image: image1.png]Table4-1  Analog Input Modules: Characteristics at a Glance

Module EUER EUE SM 33T, ST,
AIBX16bits AIBX 16 bits AIBX14bits AIBX13bits
Char High Speed
acter- (TNF00-) (TNF10) (-THFOX) (-1KFO1.)
istics
Namberof | Simputs 4 Epus 4 Binputs nd P N6
inputs channel groups | channel groups | channel groups | channel groups
Resolufion | Adistable or each | Adustable or sach | AdJustable for sach | Adjustable for each
channelgroup: | channelgroup: | channel group: | chanel group:
e15bis+slgn | e15bis+sign | e13bis+sign | 12bisssign
Measuring | Adustable for each | Adiustable for each | AQjustable fo each | Adustable for each
Method channelgroup: | channelgroup: | channel group: | channet
« Voliage « Voltage « Voltage
« Gurrent « Current « Curent * Voltage
« Curent
« Resislors
« Temperature
Selectionof | Arbirary, per ‘Arbitrary, per Arbirary, per “Arbirary
measuing | channelgroup | channel group | channel growp | per channel
range
Supports No No Yes o
clocked
operation
Programmable | Yes Yes Yes No
diagnostics
Diagnostic | Adustable ‘Adustable ‘Adustable No
interrupt
Umitvalie | Adjusiable for | Adustable for | Adjustable for No
montoring | 2 channels 8 channels 2 channels
Hardware ‘Adustable ‘Adustable ‘Adustable No
interrupt upon
timit vilation
Hardware No Yes o No
Interrupt at end
ofcycke
Potential Galvanic solation | Galvanic isoation | Galvanic solation | Galvanic solation
reationships |t © to to
«cpy «cPU o cPU Py
« Load voltage (not
for 2-DMU).
Permitied 50VDG 60vDC VDG 20v0C
potential
diterence
between the
inputs (ECM)
‘Spectal - B - -
Features
Sign Sion
2DMU 2w transiter

44

ProgrammablsLogic Controllers S7-300 Module Data

“ASE00105505.02






[image: image2.png]Table4-2 Analog Input Modules: Characteristics at a glance (continued)

Module SM 331 SW331; SM33T; ELE
AIBx12bits A8 XRTD AIBXTC AI2x12bits

Char
acter- (TKF02,) (7PF00.) (7PF10) (7KB02)
istics
Number of Binputs N4 Tputs 4 Thpus na Tinputs 1
inputs channel groups | channel groups | channel groups | channel group
Resolution "Adustable for each | Adustable for each | Adjustable for each | Adjustable for sach

channel group: | channel group: channel group: channel group:

« 9 bits+sion e15bits+sign [+ 15bits+sign |« Obitsesion

« 12 bits#sion « 12 bits+sign

« 14 bitstsion * 14bits+sign
Measuring "AGUSIaDIE for each | Adustable for each | Adjustable for each | Adustable for each
Method channel group: | channel group: channel group: channel group:

* Votage * Resistors o Temperature |« Voltage

* Curent « Temperature « Current

* Resistors « Resistors

« Temperature * Temperature
Selectionof | Amitrary, per ‘Arbirary, per “Arbirary, per “Arbitrary, per
measuring channelgroup | channel group channel group channel group
range
Programmable | No Yes Yes Yes
diagnostics
Supports Yes No No No
clocked
operation
Diagnostic ‘Adustable ‘Adustable ‘Adustable ‘Adjustable
interrupt
Limivalue | Adjustable for ‘Adjustabie for “Adjustable for “Adjustable for
monitoring 2 channels 8 channels 8 channels 4 channel
Hardware ‘Adustable ‘Adustable “Adustable ‘Adjustable
Interrupt upon
limit violation
Hardware No ‘Adustable ‘Adustable No
intermupt at end
of eyele
Potental Galvanic solaion | Galvanic fsolation | Gaivanic isolaion | Gamvanic oiation
relationships | to to to to

ecpy cru o cPU «cPu

« Load voltage (not « Load voltage (not

for2-DMU) for 2-DMU)

Permitted 25V0C 75VDC/G0VAC | 75VDC/60VAG |25VDC
potertial
diference
between the
Inputs (ECM)
Special = = =
Features
Sgn Sian
20MU 2-wire transmiter

ProgrammableLogic Controlers S7-300 Module Data

ASEDD105805.02

45







