常用功能块（FC105、FB41、FB43）课程

目的：FC105的使用

1、 FC105是处理模拟量（1~5V、4~20MA等常规信号）输入的功能块，在
[image: image1.png]


中，打开Libraries\standard library\

Ti-S7 Converting Blocks\fc105,将其调入OB1中，给各个管脚输入地址；如下：


[image: image2.png]ILAD/STL/FED - [0B1 -- XIAO\SIMATIC 300(1)\CPU 315-2 DP]
3 Fle Edt Insert PLC Debug View Options Window telp

D[3-(a] S &[®le] o[ cildl [ @f @kl 1H4#0!

Program clements Fl
0Bl : "Main Program Sweep (Cycle)”
(Comment: Qe 2l

@8 Progrem control
@ shitRotete

) Stetus bits:

@ Tiners

@ wordlogic

i FBblocks

@ FC bocks

3 5B bocks

8l SFCblocks

) Muliple instances

5l Lbreres
PTv2s6 I RET_VAL-mvso i smanc Ner_ce

5 il Standard Lbrary

@ System Functon Blocks

@ 5557 Converting Blocks

@ IEC Function Bocks

@ Organization Hocks

3 PID Control Blocks

@3 Communicaton Blocks

53 T157 Converting Blocks
HFERD LEAD LAG
hFER1 DCAT
ThFER MCAT
ohFEes MC

SCALE | CONVERT

THCALE”
n Enof

5.000000e+ 0UTf-1m200
000 ur_1m

0.000000e+
000 o
m.o

1 ——fpreouir

|2






[image: image3.png]#HLAD/STL/FBD - [0B1 -- XIAQ'\SIMATIC 300(1)\CPU 315-2 DP]
3 Fle Edt Insert PLC Debug View Options Window telp

Dls(e-8] & dlesle] S|-| el s o) L0 ) i

O0BL : “Main Program Sveep (Crele)r  TRRTErTS A

Sroo ww A
Srca wRoTL
Srem sw F
Srem s
Sres am 8
Sres
Sroms o L
Srcwr oeco
cau scae Srcm oo
w zs6 Srcsn o
FI_LIH :-5. 000000e+000 Srco rsen
LoTLTn -0.0000002+000 Sran s
BIPOLAR: -FALSE Srae oev
Sram wr
Srcios T
o
Srcie e T
SCALE | CONVERT

[Comment:

[Conment:





其中，管脚的定义如下：

IN---------模拟量模块的输入通道地址，在硬件组态时分配；






HI_LIM---现场信号的最大量程值；






LO_LIM--现场信号的最小量程值；

BIPOLAR—极性设置，如果现场信号为+10V~-10V（有极性信号），则设置为1，

如果现场信号为4MA~20MA（无极性信号）；则设置为0；

OUT-------现场信号值（带工程量单位）；信号类型是实数，所以要用MD200来存放；

RET_VAL-FC105功能块的故障字，可存放在一个字里面。如：MW50；

2、 热电偶、热电阻信号的处理，该类信号实际值是通道整数值的1/10；


[image: image4.png]o Ex) VR
e Ew0 e Ew0 e EwO
pruzeo—{I___ ovThmizo w1z 0Tl miza WizamL  OUTp1za

1.000000e+
001 {2





3、 FB41 PID控制模块的使用；

PID模块是进行模拟量控制的模块，可以完成恒压、恒温等控制功能 在
[image: image5.png]


中，打开Libraries\standard library\

PID Control block\FB41,将其调入OB1中，首先分配背景数据块DB41，再给各个管脚输入地址；如下：


[image: image6.png]ILAD/STL/FBD - [0B1 IMATIC 300(1)\CPU 315-2 DP]
b Fle Edt Insert PLC Debug View Options Window telp

w1 (=] [alml@] [=e] o] (=] [ 0By G ] QHORLIET []

oaL B9 ew network
oA i Bt logic
e mo & Comparator
& Converter
lcom s sz & Counter
ol DB cal
102 -mn_ow Lm_pER, (& 2umps
& nteger fet
eveeron qumi s &8l Floatig:poirt ft
@ vove
e QUL - G Program contral
. . @ shitRotete
= = ) Statusbits
| 0w 1 (o Timers
& Wordlogc
domon o e FB locks
@ FCblacks
p_sen w & 578 bocks
& SFCHlocks
. evee £R| 1 Mutile stances
5l Lbreres
miz0-{sP_TT E Y
&l tandard Lbra
miza-{F_In & Svstem Fun
& 5557 Con
- PrrER B TEC Funcir
@ Organizati
i
iz £l PID Control
oamw o et
Fen
n ren
& Commurica
Jm & 1157 Conv
M xizng
S tas






[image: image7.png]Symbol information:

FEAL cam_¢ Continuous Control
0.2 TICOD0L i

120 TIC0001_SET

124 TI0001 R

128 TICo00L M

m13z TIc0001 OUT





4、脉冲输出模块FB43，该模块是将模拟量转换成比率的脉冲输出。Libraries\standard library\

PID Control block\FB43,将其调入OB1中，首先分配背景数据块DB43，再给各个管脚输入地址；如下：


[image: image8.png]{i#LAD/STL/FBD - [0B1

test|SIMATIC 300(1)\CPU 315-2 DP]

£ Bl Edt Insert PLC Debug Vew Options Window telp

MEIE
=181

w5 [ (=] [lmli] [=[e] o] [=] [ [<bY G [ ] QHORL]ET [ ]

B4z

o

13z IV

per_TH aEs
5

RATIOFAC

sTERS_on

s12BT_on

masr_on

pos_p_ow

eG_e_ow

sv1_ow

con_rsT

cveie

B
1

r0s_plqo.7

Symbol information:

B4
w13z

PULSEGEN Pulse Generation

TIc0001_OUT

K]

o

B9 ew network

&l Bitlogic

& Comparator

&3 Comverter

&1 Counter

& 0B cal

& Jumps

@0 Tnteger fe

& Fosting-port ft.

@ Move

@8 Progrem control

@ shitRotete

) Stetus bits:

@ Tiners

@ wordlogic

i FBblocks

@ FC bocks

3 5B bocks

8l SFCblocks

) Muliple instances

5l Lbreres

A saTICNET P

Standard Library

@ System Functon Blocks

@ 5557 Converting Blocks

@ IEC Function Bocks

@ Organization Hocks

53l PID ControlBlcks
TFBA CONTC
ThFe CONTS
PB4 PULSEGEN

&3 Communicaton Blocks

@3 T157 Converting Bocks

M 5era

PULSEGEN | ICONT %

=

AL DI Erres

Tnf;

Press Fi to get Help.

|| B) ) @ 6 || #awancm.. |[Fiaostrs.., CusraoniEtt.. | Esteer 230, | Sk - mE|

[ © fofine

s w2 finsert |

Dot (S ML EE 145




将程序下载调试，看PID的温度调节作用如何？如果控制的不好，改变P、I参数！

5、 果现场是阀门等执行机构，只需要将通道地址输入PID的输出通道，如下：


[image: image9.png]B4l

FBaL
e ol
con_rsT 1

10.2-{mAN_ow Lm_pER,
prER_on  oumi_mn
»_sEL Qum_Lix
1 _sEL mp
1r_sowp 1
_1m_ow 1 p
p_seL w
croe ®





6、如果单独控制变量输出通道，可使用FC106模块，FC106是处理模拟量（1~5V、4~20MA等常规信号）输出的功能块，在
[image: image10.png]


中，打开Libraries\standard library\Ti-S7 Converting Blocks\fc106,将其调入OB1中，给各个管脚输入地址；如下：
[image: image11.png]$LAD/STL/FBD - [0B1 SIMATIC 300(1)\CPU 315-2 DP]
b Fle Edt Insert PLC Debug View Options Window telp

w5 [ (=] [ el (=] o] B0 0eDl G (1O 1T ulSP L]

Program elements:

B9 ew network
&l Bitlogic

& Comparator

&3 Comverter

&1 Counter

& 0B cal

& Jumps

@0 Tnteger fe

& Fosting-port ft.
@ Move

@8 Progrem control
@ shitRotete
) Stetus bits:

@ Tiners

@ wordlogic

i FBblocks

@ FC bocks

3 5B bocks

8l SFCblocks

) Muliple instances

8 Lbrarics

UNSCALE"
n Enof

"nan_out” —{IIl FET_vAL{so

0.000000e+ 0UT|-pawzse
000 ur_1m

1.000000e+
00z o

0. 0 —{BLPOLAR




 


[image: image12.png]









